## Table 1
Bihar Medical Services & Infrastructure Corporation Ltd, Patna
Reply to Prebid queries dated 20.04.2018
Name of Project- Construction of Government Dental College & Hospital, Paithna, Rahui, Dist-Nalanda, Bihar
Sr. No. | Clause | Clause Details | Reference / Clause no. | Queries | Clarification from Client / DAI
General & Commercial Queries
1 | Earnest Money Deposit | The Bidder shall furnish, as part of his Bid, a Bid security in the amount as shown in column 4 of the table of IFB for this particular work. This bid security shall be in favour of Employer as mentioned in the NIT and in any one of the following. a. Demand draft issued from any schedule bank in favour of the Managing Director, BMSICL., payable at Patna b. Unconditional bank guarantee from any scheduled Indian bank issued within the state in the format given in Vol. III (If issued from any bank outside state will be Converted to any bank within the state before executing the agreement. | Tender Document, Clause-16, Page 10 of 40 | Kindly furnish the format for Bank Guarantee. | Available in the tender document
|  |  |  | Kindly furnish your Bank Details including IFSC code | Firm Name-BMSICL, Bank Name-State Bank of India, Add.-Main Branch, West Gandhi Maidan, Patna Account No.-32698348321 IFSC Code-SBIN0000152
2 | EMD Value | Earnest Money Deposit - 3,69,72,000 Earnest Money - Rs. 3.70 Crore | Technical Bid Sheet, Pt.6 Notice Inviting Re-Tender, Pt.2, Page-1 | EMD value is found to be different in 2 places. Kindly confirm the exact value. | EMD Value is 3,69,72,000/-
3 | TYPE OF CONTRACT | Bids may be submitted only in - Percentage (Group A Schedule Item) and Item Rate Method (Group B Non Schedule Item) | Appendix to ITB Clause no 14 | Both the clauses are contradicting with each other, We understand design and drawings are not in contractor's scope,please clarify | Group A in percentage rate whereas group B in Item rate
|  | The scope of work covers the supply, erection, testing and commissioning of the Civil, Plumbing, Fire Fighting & Electrical Systems, HVAC -Air- conditioning, Lifts & Landscaping works which also includes design & preparation of structural and all other detailed shop drawings, testing and commissioning of components and accessories. | Clause 2.1 Additional Conditions of Contract,Page 123 of 140 |  | Design and drawing is not in the scope of contract. However services shop drawing shall be prepared by contractor or his vendor.
4 | MOBILISATION ADVANCE | 10% of the tendered value may be given bearing a simple interest 10% per annum. | GCC and SCC, Clause 10B (ii), page 21 and Schedule F Page-64, | We request you to provide us Interest free mobilisation advance amount | No change as per tender document
5 | ADVANCE AGAINST PLANT & M/C | 85% shall be paid on purchase of new plant at 10% simple interest rate. The amount so paid shall be restricted to 5% of the contract value. | GCC and SCC, Clause 10B (iii), page 21 and Schedule F Page-64. | We request you to provide us interest free advance payment For plant and machineries | No change as per tender document
6 | LIQUIDATED DAMAGES | 2% per month of delay to be computed per day basis provided always that the total amount of compensation for delay to be paid under this condition shall not exceed 10% of the Tendered Value of work . | GCC and SCC , Clause 2, page 8 | We request to recover LD @ 0.25% of the balance work value per week of delay subject to maximum of 5% of Balance Job value. | No change as per tender document
7 | RETENTION MONEY | 8% of Contract Value (CV) to be deducted from RA Bills. Total Security - 10% of CV including 2% of Performance Security & EMD. | GCC and SCC, Clause 1A page-8, and Schedule F page 64. | We request you to keep the Total limit of Retention money as 5% of Contract Value and request you to accept Bank Gurantee in Lieu of Cash Retention | No change as per tender document
8 | MONTHLY RA BILL | Monthly R A Bills shall be for a minimum value of 10 Crore. | Schedule F Page 66.Clause-7 | We request you to reduce the minimum value of Rs. 10.0 Crore to Rs 4.0 crore for first 3 nos RA bill and for last 1 no RA bill | Accepted
9 | PAYMENT OF FINAL BILL | Payment of Final Bill will be made within 4 months from the date of receipt of the Bill | GCC and SCC, Clause 9 page 17. | We request to keep the date of Payment of Final Bill as 2 months from the date of receipt of the Bill | No change as per tender document
10 | LABOUR CAMP | The Contractor shall make arrangements for the engagement of all staff and labour, local or otherwise, and for their payment, housing, feeding and transport. |  | Since sufficient land is available, we presume that arrangement for labour hutments can be made inside the site premises. We request you to provide us land for labour hutment, store, batching plant and other infrastruture setting free of cost within site premise | Contractor has to arrange land for labour hutment, store, batching plant etc. if required to be established outside of campus at his own cost and risk.
11 | CONSTRUCTION WATER | The contractor shall make his own arrangement for obtaining electric connection required for execution of work and make necessary payments directly to the concerned departments and nothing extra shall be payable on this account. | GCC and SCC, Clause 5 page 79 | We request you to provide us Construction Water free of Cost at one point. Distribution arrangement will be done by us. | No change as per tender document
12 | CONSTRUCTION POWER | The contractor shall make his own arrangement for obtaining electric connection required for execution of work and make necessary payments directly to the concerned departments and nothing extra shall be payable on this account. | GCC and SCC, Clause 5 page 79 | We request you to provide us Construction Power free of Cost at one point. Distribution arrangement will be done by us. | No change as per tender document
13 | TAX | Sales Tax or any other tax on materials in respect of this contract shall be payable by the contractor according to law in effect. | GCC and SCC, Clause 34 page 53 | As GST is applicable wef 01/07/2017, so we presume that GST will be applicable Kindly confirm the applicable rate of GST for this Package | Bidder is requested to bid his rate including GST etc. Nothing extra shall be pain on account of this.
14 | ARBITRATION | To proceed for Arbitration, the first mandatory step is to seek a written decision within seven days of the occurrence of the matter to the Chief General Manager, who in turn shall reply in writing within 15 days of rceipt of that. Within the next 15 days the contractor should appeal to the Chief General Manager who shall convey within 30 days his consideration. within 30 days the contractor serve notice for appointment of Arbitrator to the Chief General Manager failing which there will be no arbitration. The matter may be referred to Adjudicator appointment by the Engineer-in-Chief when the client's decision is final. (Place of arbitration will be Patna. The arbitration shall be conducted in accordance with the provisions of the Arbitration and Conciliation Act 1996 (26 of 1996) | GCC and SCC, Clause 25, page 45. | WE request to constitute Arbitration Panel of 3 Arbitrator,one each from either party and a Nuetral Arbitrator | No change as per tender document
15 | MILESTONE LD | Also 0.5% of CV will be held for failure of each Mile stone as per Mile stone chart | Schedule F - Mile stone Table, page 66 | Kindly clarify whether 0.5% of milestone work will be withheld as LD for failing to achieve each milestone as per chart | No change as per tender document
16 | Tree cutting |  |  | Any permission for trees cutting will be taken by Client,Please confirm | Permission required for tree cutting will be taken by contractor. All necessary help will be provided by BMSICL.
Technical Queries- Civil
1 | TOPOGRAPHY | Not provided. |  | We request you to provide the Topography/Contour of the site | Drg attached However bidders to check and do there own survey.
2 | Architectural - Autocad drawings | Not provided. |  | Please provide all Architectural plans including site plan in Autocad format. | Please find enclosed drawings in pdf format.
3 | Soil Report | Not provided. |  | Kindly provide us the Soil Report | Soil report attached However bidders to check and do there own survey
4 | Pile work | Boring, providing and installing bored cast-in-situ reinforced cement concrete piles of grade M-25 of specified diameter and length below the pile cap, to carry a safe working load not less than specified, excluding the cost of steel reinforcement but including the cost of boring, with bentonite solution and temporary casing of appropriate length for setting out and removal of same and the length of the pile to be embedded in the pile cap etc. all complete, including removal of excavated earth with all lifts and leads (Length of pile for payment shall be measured upto bottom of pile cap). | BOQ - Schedule items ,Serial no- 34,BSR_20.2 | Kindly mention the minimum cement content and also provide the pile drawing | Minimum cement content will be as per Bihar SOR/ IS Codes.
5 | Isolation Bearing | Design, Manufacturing, Supply, installation of lead rubber bearings(LRB) of approved make for base isolation system or seismic isolation to meet the system adequacy requirement based on load combinations . | BOQ - Non Schedule items ,Serial no- 17 | Kindly specify the Column Load to be considered for the Designing of lead rubber bearings for base Isolation system | Column load is attached as annexure. Please note base isolation will be as per manufacturer's specification confirming to load requirement.
6 | Kitchen Item | Kitchen Equipments for Hospital | BOQ - Non Schedule items ,Serial no- 623-672 | Kindly Specify the approved make of the Items | Attached specification & LOM.
7 | Laundry Item | Laundry Equipments | BOQ - Non Schedule items ,Serial no- 586 - 595 | Kindly Specify the approved make of the Items | Attached specification & LOM.
8 | Medical Gas pipeline | Medical Gas Pipeline System | BOQ - Non Schedule items ,Serial no- 573-585 | Kindly Specify the approved make of the Items | Attached specification & LOM.
9 | TSSU Equipment | TSSU Equipments | BOQ - Non Schedule items ,Serial no- 612-622 | Kindly Specify the approved make of the Items | Attached specification & LOM.
10 | CSSD Equipment | CSSD Equipments | BOQ - Non Schedule items ,Serial no- 596-611 | Kindly Specify the approved make of the Items | Attached specification & LOM.
11 | IV tree System | IV TREE SYSTEM | BOQ - Non Schedule items ,Serial no- 673 | Kindly Specify the approved make of the Items | Attached specification & LOM.
12 | Siloxane | Applying breathable, non-reactive, antifungal, and water repellant Silane/ Siloxane chemical as approved by Archaeological Survey of India/ Engineer-in-charge, of approved brand and manufacture, diluted with solvent mineral Turpentine oil in the ratio of 1:12 (One part of approved chemical :12 Part of Turpentine oil), on the existing sand stone masonry surface with two or more coats to give uniform application of chemical on the surface, all complete as per direction of Engineer-In-charge (The rate is inclusive of all materials & labours involved except scaffolding). | BOQ - Schedule items ,Serial no- 90 | Kindly mention the specification of the item and the approved make of the same | Hinduatan Alcox Ruisilicone Baker or equivalent
13 | 1st quality ceramic glazed wall tiles | Providing and fixing 1st quality ceramic glazed wall tiles conforming to IS : 15622 (Thickness to be specified by the manufacture) of approved make in all colours, shades except burgundy , bottle green | BOQ - Schedule items ,Serial no- 57 | Kindly mention the size of the Tiles | To be 300X450mm/ Bihar SOR.
14 | Nurse Call System | NURSE CALL SYSTEM | BOQ - Non Schedule items ,Serial no- 674 | Kindly give the Spec and Breakup of the BOQ | Attached specification & LOM.
15 | Pneumatic Tube System | Pneumatic Tube System | BOQ - Non Schedule items ,Serial no- 674 - 685 | Kindly Specify the approved make of the Items | Attached specification & LOM.
MEP Works
1 | PLUMBING | General |  | Please provide Catalogue No of all Sanitary ware and CP fittings. | It should be as per specification and description of BOQ. LOM already provided.
| PLUMBING | General | TECHNICAL SPECIFICATIONS: PLUMBING & FIRE-FIGHTING | Please provide Technical Specification for Borewells. | Please refer to CPWD specification and BOQ language sufficient enough for quoting
| PLUMBING | General |  | Please provide List of Approved Make of Materials for STP, WTP & RO plant. | Attached specification & LOM.
2 | HVAC | List of Approved Makes of Materials |  | Approved make for AHU is not mentioned. Kindly confirm the same. | Refer HVAC Specification.
| HVAC | Humidification Package | HVAC BOQ: Item No: 461 | Description of the item is not clear. Please describe in detail. | Refer HVAC Specification.
| HVAC | General |  | Approved make for Ventilation Fan is not mentioned. Kindly confirm the same. | Refer HVAC Specification.
| HVAC Contractor | Approved List Of HVAC Contractor For Complete HVAC Package | SCHEDULE OF APPROVED HVAC CONTRACTOR & MAKES: 11-A | We would equest you to coonsider 'Suvidha Engineers India Pvt. Ltd .' and 'Zamil Air Conditioners india Pvt Ltd.' as approved HVAC contractors. | Will be approved by BMSICL on receipt of shop drawing at the time of execution.
| Chiller | Approved List Of Make | SCHEDULE OF APPROVED HVAC CONTRACTOR & MAKES: 11-B | We would equest you to coonsider 'Clivet' as approved make of chiller. | Given LOM to prevail.
| Pump | Approved List Of Make | SCHEDULE OF APPROVED HVAC CONTRACTOR & MAKES: 11-B | We would equest you to coonsider 'Wilo' as approved make of Pumps. | OK
3 | ELECTRICAL | DG | LIST OF APPROVED MAKES FOR: ELECTRICAL WORKS: | We request you to please include Perkins as approved make. | Given LOM to prevail.
| ELECTRICAL | Light Fittings | LIST OF APPROVED MAKES FOR: ELECTRICAL WORKS: | Please provide Catalogue Number and List of Approved Make of Materials for Light Fitting. | It should be as per specification and description of BOQ. LOM already provided.
| ELECTRICAL: UPS SYSTEM | Supply, installation, testing & commissioing of UPS in paralleling mode at 0.99 input power factor with SNMP card, compatible for BMS connectivity on backnet/MODBUS, inbuilt isolation transformer as per specification given in the document with following broad features | BOQ- ELECTRICAL WORKS: SL NO- 313 TO 320 | Some of the approved manufacturers are unable to provide UPS with 'inbuilt isolation transformer'. So we would request request to kindly accept UPS with external isolation transformers also. | BOQ specifications will prevail.
4 | BMS SYSTEM | General | LIST OF APPROVED MATERIALS | Kindly provide list of approved materials for BMS System. | Already available in tender LOM.
Sr. No. | Clause | Clause Details | Reference / Clause no. | Queries | Clarification from Client / DAI
1 |  | i. At least one hospital or composite hospital campus having College/Hostel/Residential Building (including civil works along with services like plumbing, electrical, HVAC etc.) having total cost not less than 40% of the estimated value (i.e. Rs. 143.89 Cr.) of the project put to tender. |  | At least one hospital or composite hospital campus having College/Hostel/Residential Building/Ancillary Building (including civil works along with services like plumbing, electrical, HVAC etc.) having total cost not less than 40% of the estimated value (i.e. Rs. 143.89 Cr.) of the project put to tender. | No Change as per tender document.
2 |  | At least one hospital or composite hospital campus having College/Hostel/Residential Building (including civil works along with services like plumbing, electrical, HVAC etc.) having total built up not less than 40% of the project (i.e. 35161 Sqm)put to tender. |  | At least one hospital or composite hospital campus having College/Hostel/Residential Building/Ancillary Building (including civil works along with services like plumbing, electrical, HVAC etc.) having total built up not less than 40% of the project (i.e. 35161 Sqm)put to tender. | No Change as per tender document.
Sr. No. | Clause | Clause Details | Reference / Clause no. | Queries | Clarification from Client / DAI
1 | Clause 10B iv & Schedule F | The mobilization advance and plant and machinery advance bear simple interest and should be equal to the Prevailing rate of interest charged by the bank as mentioned in contreact dat schedule F (10% P.A. simple interest) | Clause 10B iv & Schedule F | We request you to provide interest free mobilization. | No Change as per tender document.
2 | 41 | On completion of the whole of the work, half of the total amount of security shall be repaid to the contractor after six months of completion. However, the balance half of the total amount of security will be returned after completion of defect liability period and after the Engineer has certified that all defects notified by him to the contractor before the end of this period have been corrected and also after recovery of any dues |  | We propose to submit a Bank Guarantee @ 8% of contract value at the beginning of the execution against retention money instead of deduction of the same from the RA bills for better cash flor, Please confirm | No Change as per tender document.
3 |  | Bank details of Client |  | We request you to provide the bank details to enable us to make the Bank Guarantee
4 | Schedule F | Defects liability period is 36 Months from date of completion |  | We request you to make the defect liability period as 12 months instead of 36 months.
Sr. No. | Clause | Clause Details | Reference / Clause no. | Queries | Clarification from Client / DAI
General/Civil Works
1 |  | EMD |  | Please provide benificiary account details for preparation of Bank Guarantee towards Earnest Money Deposit.
2 | GCC Schedule F clause No. IV | Defect Liability Period | 36 Months | As per normal industry practice defect liability period should be 12 months. Please confirm. | No Change
3 | Clause 7 | Gross work to be done together with net payment/ adjustment of advances for material of collected, if any, since the last such payment for being eligible to interim payment | 10 Crores | We request you to relax minimum bill value in initial Four RA bills. | Accepted
4 |  | GST | Not mentioned | Please mention applicable GST percentage on this project. | Bidders are requested to bid his rate including GST etc. Nothing extra shall be pain on account of this.
5 |  | Seigniorage Fee |  | As per Govt. of Bihar Notification 2% Seigniorage Fee to be imposed on Every tender. Kindly Clarify whether it is included in estimated cost of the tender. | Bidder is requested to consider all levy/Seigniorage Fee etc. imposed by Govt. of Bihar in his bid, as per provisions of law
6 |  | Release of Retention Money | Half of the total amount of security shall be repaid to the contractor after six months of completion. However, the balance half of the total amount of security will be returned after completion of defect liability period. | Retention money should be released against Bank Guarantee on every accumulation of Rs. 5 lacs as & when required by us. | Will be released as per Govt. rule.
7 |  | Space for batching plant & labour hutment |  | We understand that space for batching plant and labour hutment will be provided within the site campus. Please confirm. | Contractor has to arrange land for labour hutment, store, batching plant etc. if required to be established outside of campus at his own cost and risk.
8 |  | Performance Guarantee | The performance Guarantee shall be initially valid up to 28 days beyond the defect liability period (3 Years). | As per normal industry practice Bank Guarantee towards performance should be valid upto completion period + 60 days. In CPWD performance guarantee is upto completion period, please review and modify. | No Change
9 |  | Bid Submission Date |  | Please extend Bid submission date by 2 weeks. | No Change
Technical
BOQ Schedule Items
1 | Items No. 47 to 49 | Expension Joint |  | Mention approved vendor for expension joint. | C.S, HERCULUS, Z-TECH, VEXCOLT, FISCHER, HILTI
2 | Items No. 27 & 28 | PVC door frame & PVC door shutter |  | Specify the approved make for the same. | FENESTA, WINTECH, ALUPLAST, STAYBRIGHT, WINDOWMAGIC, LG, FIXOPAN, FIBRE WAYS, AQUA CELL, JAI SHREE, SINTEX, ECODUR
3 | Items No. 36 | UPVC window |  | Specify the approved make for the same. | FENESTA, Rahoo, WINTECH, Sintex, PSP
4 | Items No. 17 | Lead rubber bearings |  | Specify the approved vendor for lead rubber bearings also the unit of the item should be in number. Please clarify. | ITEM IS IN NUMBER'S ONLY APPROVED VENDOR'S ARE ROBINSON, DIS OR EQUIVALENT
5 | Items No. 20 | 18 mm thick 150 mm wide pelmet |  | Unit of this item should be in RMT. | AS PER BIHAR SOR 2016 UNIT IS IN SQM.
6 | Items No. 32 | Auditorium seating |  | Unit should be in numbers. | Sl. No. 33 (NSI) Auditorium seating unit will be no.
7 | Item No.88 (SI) | Structural Steel frame work for stone cladding |  | Unit of this item should be in Kg. | Ok Correct unit is Kg.
8 | Item No. 132 (SI) | Granite Stone block |  | Unit of this item should be in sqm. | Ok Correct unit is Sqm.
9 | Items No. 102 | Designing, fabricating, testing, installing and fixing in position Curtain Wall with Aluminium Composite Panel Cladding |  | BOQ description is at varience from description mentioned in DSR 2016. As per DSR Base frame work for ACP cladding is payable separately under the relevant aluminium items. Whereas it is not mentioned in BOQ item description. Also tests as mentioned in BOQ item description is not in DSR item. Please correct the BOQ item description in line with DSR and incorporate in revised BOQ. | ITEM DESCRIPTION IS ONLY FOR ACP AS PER DSR NOT FOR CURTAIN GLAZING
BOQ Non Schedule Items
1 |  | Furniture works |  | Mention approved makes for furniture items. | GODREJ, B.P ERGO, WIPRO, FEATHERLITE, HERMAN MILLAR
2 |  | Modular OT, Medical gas sustem, laundry equipments, CSSD equipments, TSSU equipments, kitchen equipments, IV tree system, Nurses call system & Signages |  | Please provide technical specifications for these items also provide approved makes and apporoved vendors for these items. | MAKE AND SPECIFICATION IS ATTACHED
3 | BOQ Item no. 22 | Gypsum False Ceiling | BOQ Item description Last line "Finishing with 21 or more coats of plastic emulsion paint." | It should be "Finishing with 2 or more coats of plastic emulsion paint." | Ok Corrected
4 | BOQ Item no. 25 | Accoustically Absorbptive Ceiling |  | Mention the quantity of Black Matt Ceiling. | RATE ONLY ITEM
5 | BOQ Item no. 33-61 | Speakers and Accessories |  | Unit of this item should be in No. Kindly clarify. | Ok Corrected
6 | Sl no. 59 | Approved make in Make list |  | We propose to add " Sukri" Brand in approved makes for fire door for Competitive rates. | OK, PROVIDED THIS BRANDS FULL FILL THE INDIAN CODAL REQUIREMENT AND BOQ SPECIFICATIONS
7 | Sl no. 60 | Approved make in Make list |  | We propose to add " Pyroguard UK "and "Schott Germany" Brand in approved makes for fire rated Glass for Competitive rates. | OK, PROVIDED THIS BRANDS FULL FILL THE INDIAN CODAL REQUIREMENT AND BOQ SPECIFICATIONS
8 | Sl no. 63,65,66 & 67 | Approved make in Make list |  | We propose to add " Marshall " Brand in Fire Rated hardware approved makes for fire rated hardwares for Competitive rates. | OK, PROVIDED THIS BRANDS FULL FILL THE INDIAN CODAL REQUIREMENT AND BOQ SPECIFICATIONS
ELECTRICAL WORKS
Bill of Quantity (BOQ-GROUP B)
1 | Item No 33 to 61 | SOUND REINFORCEMENT SYSTEM | For Example:- 33) Two-Way Line-Array Loudspeaker System with 1x12" / 2x8" LF & ≥2 HF components on constant curvature waveguide; for Passive or Bi-Amplified Operation, as per specifications (4+4+4 for L-C-R) - 12 Sqm | 1) The Unit will be either in Nos or in Sets instead of "SQM". Please confirm/Clarify. 2) The technical specifications are not in the tender document, Request to furnish for the same. | OK, CORRECTED TECHNICAL SPECIFICATION ARE ALWAYS MANUFACTURER SPECIFIC HENCE , BOSCH, BOSE, JBL
2 | Item No 199 to 242, 246, 250, 254, 258, 263 to 266 & 398 to 402. | LT Panel | All the MCCB up to 250 Amp shall have thermal release with adustable overload, short circuit & earth fault protection and above shall have microprocessor release with adjustable overload, short circuit & earthfault protection. The panel shall be manufactured as per BOQ, tech specification and drawing. | All MCCBs( Incomer/ outgoing) are with Earth Fault Protection, The Earth fault is not required for Outgoing MCCB,Only Incomers shall have Earth Fault Protection, Please Clarify/Confirm. | BOQ LANGUAGE AND SPECIFICATION WILL PREVAIL
3 | Item No 243, 247, 251, 255 & 259. | Rising Main | Design, Manufacturing, Supply, Receiving, Unloading, Shifting, Installation, testing and commissioning of following capacity Rising Mains consisting of total metal enclosure, TPN high electrolytic conductivity aluminium conductor bus bars fully covered with heat shrinkable PVC coloured sleeves, suitable for operation on 415 V / 650 V 3 phase, 4 wire 50 cycles AC supply system. The construction should be such that it will be dust and vermin proof to IP 42 in 2mm thickness and front cover in 1.6mm thickness CRCA powder coated sheet construction. The Rising Mains should be built in convenient sections complete with fire proof barriers, thrust pads, expansion joints at intervals and straps for fixing on wall or floor mounted arrangement duly marked with the current carrying capacity. The entire length should be fitted with a double run of aluminium earth strip of suitable size. Rising Main shall be comply fully with specification. | Breaking Capacity in KA not mentioned, Please Provide. | 36KA
4 | Item No 267. | MAIN & SUB MAIN CABLES | Supply of following sizes of 1.1KV grade multicore aluminium conductor XLPE insulated and FRLS PVC sheathed armoured cable conforming to relevant IS. (Cable shall be purchased only after approval of cable schedule by architect / consultant) | Whether inner sheath FRLS, or outer sheath FRLS or both inner & Outer sheath FRLS required, Please Clarify & Confirm. | OUTER FACE FRLS
5 | Item No 279 to 294.etc. | Lighting Fixture | For Example:- Supply, Installation, Testing & Commissioning of 1x28 watt CFL light fixture for Kitchen surface mounted including electronic ballast etc complete as required. (Philips Make, Cat No - V2 VECTOR 28 W TCH 207 or equivalent.) | Please note that nowdays LED Type Lighting Fixtures are used everywhere, with CFL Light fixture are phase out most of manufacturers.therefore we request you to please provide Cat No of LED Lighting fixtures in place of conventional fixtures (CFL/HPSV) where ever mentioned on BOQ, please clarify & Confirm. | LED TYPE MOISTURE PROOF FIXTURE TO BE CONSIDERED MATCHING WITH LUX LEVEL REQUIRED
6 | Item No 385. | Lifts | 9 Passenger Lift | The 9 passanger Lift is not as per manufacturer standard, they have either 8 passanger or 10 passanger, Please Clarify & Confirm. | TO BE READ AS 8 PASSENGER LIFT
7 | Item No 436. | Solar Sytem Works | Supply, Erection and Testing Solar Panel (MCA‐205 - 200 W) x 250 pieces + solar outdoor Junction box + Solar Inverter grid‐connect (50 kw) + Cable upto AC panel + solar mounting structure + AC panel with MCCB surge protectionand energy meter with digital outer protection + Data Logger. | Make & Technical Specifications required, Please provide. | MNRE APPROVED TECHNICAL SPECIFICATIONS TO BE FOLLOWED APPROVED VENDOR'S ARE TATA SOLAR POWER, BHEL, PHOTON, TOPSUN, DESHMUKH, POWERTECH, INDOSOLAR, NOVERGY, KIRLOSKAR, ADANI
8 |  | List Of Approved Makes |  | There are two List of approved makes provided with the tender document one with technical specifications & another seperately, please specify which one is to be considered, Please Clarify. | BOTH HAS TO BE CONSIDERED FOR BROADER POOL OF MAKES
ELECTRICAL WORK SPEC
9 | 1.1 | PRICES,UNIT RATES & TAXES / DUTIES ETC: | a) The prices and unit rates quoted by the bidder in the bid shall be firm and deem to be adequate to cover the entire responsibility involved in the execution and completion of work. The rates shall be complete in all respects including cost of materials, erection, fabrication, labour, supervision, tools and plant, transport, contingencies, breakage, wastage, sundries, scaffoldings, insurance & all government levies such as excise, sales tax, WCT, VAT, SERVICE TAX etc. b) The contract value shall be inclusive of custom duty, CVD etc on Imported Equipments & also inclusive of excise duty & inclusive of VAT / local sales tax on indigenous Equipments / Materials and inclusive of octroi duty or any other duties or fees levied by government or any public or local bodies. | Please note that now GST is applicable from july 2017, so please modify this clause, Please Clarify/Confirm. | GST WILL ONLY BE APPLICAL AS PER NORMS. Bidders are requested to bid his rate including GST etc. Nothing extra shall be pain on account of this.
10 | 3.1.15 | DG SET | FUEL TANK: Day service fuel tank shall be made of 3mm thick MS sheet of 990 litres capacity for each set with all accessories such as oil level indicator, inlet pipe connection, outlet pipe connection, trough to collect split oil, air vent pipe with air filter, manhole with cover, low level and full level float valve arrangements with all fittings interconnections between tanks. The tank shall be provided with suitable calibration scale. | The Fuel tank shall be made of 2mm Thick in place of 3 mm as per manufacturer standard, Please Confirm. | BOQ LANGUAGE AND SPECIFICATION WILL PREVAIL
11 | 3.12 | 33KV/0.415KV DISTRIBUTION TRANSFORMER | LOAD LOSSES : AS per IS 1180 Level1. | In specification Level 1 Load Loses are considered, whereas nowdays Level 2 is applicable, Please Clarify/Confirm. | LEVEL 2 TO BE FOLLOWED
12 | 3.21 | PUBLIC ADDRESS SYSTEM | The planning and invitation to tender are based on Honeywell's VARIODYN D1 model. Equivalence must be ensured in the case of alternate offers as these are based on customer-specific assessments of requirements. | In the specification Honeywell make/ model no is specified, we request you to review specifications, so that at least two-three makes can meet the specifications/comply, Please Clarify/Confirm. | IT SHOULD BE READ AS OR EQUIVALENT
13 | 3.22.36 | UPS SYSTEM | SPARE PARTS The recommended spare parts for 5 years of maintenance are to be listed and should be quoted along with main modules. | In Boq there is no line item specified to quote for Spare Parts for 5 year maintenance, we request you to furnish the same enabling us to quote for the same, please confirm/clarify. | TO BE INCLUDED IN QUOTE BY BIDDERS AS PER UPS MAINTAINANCE MANUAL GUIDELINES
14 | 60 | DG SET | D.G. Set (Engine) - Cummins - Catter Piller - MTU | We request you to please give approval of M/s Perkin make for Dg Engine, Please confirm. | ONLY SPECIFICED LIST TO BE FOLLOWED
15 | 66 | DG SET | D.G. Accoustic Enclosure - Cummins - Sterling - Catter Piller | The approved make M/s CUMMINS does not manufacturer the DG Accoustic Enclosure, We request you to give approval of the system houses of these brands for Accoustic Enclosure, Please Confirm. | IT SHOULD BE DONE AS PER OEM APPROVED VENDOR
LIFT WORK SPEC
16 | 2.1 | LIFT | The lifts shall be A.C. variable voltage variable frequency micro processor controlled Machine Room & Machine Room Less as specified in BOQ. | It is not clear whether the required lift is with Machine Room(MR) or Machine Room Less(MRL), Please Clarify/Confirm. | PLEASE REFER TO BOQ LANGUAGE/ARCH DRAWING
HVAC WORKS
1 | BOQ Sr. no- 437 | Chiller | ARI certified chiller | Please approve GB certified chiller | ONLY ARI TO BE FOLLOWED
2 | BOQ Sr. no- 437 | Chiller | COP at AHRI condition - 6.2 (min) | Please accept COP at 5.8 as per ECBC norms | OK
3 | BOQ Sr. no- 437 | Screw Compressor | No. of compressor per chiller is not mentioned | It is recommended to have multiple circuit for large capacity of 250TR | NO CHANGE IT SHOULD BE AS PER TENDER SPECIFICATION
4 | BOQ Sr. no- 437 | Chiller | Power Consumption Of Chiller / TR At Tender Condition Mentioned Above (Max) - 0.68 | Please accept power consumption of chiller/TR at tender condition - 0.7 (Max) | NO CHANGE IT SHOULD BE AS PER TENDER SPECIFICATION
PLUMBING WORKS
1 | BSR-16.17.38 | Providing & Fixing of C.I. Bend |  | Rate of 75mm dia Bend is not mentioned in BOQ | 75MM DIA NOT REQUIRED
2 | BSR-16.17.43 | Providing & Fixing of C.I. "Y" & "TEE" |  | Rate of 75mm dia "Y" & "TEE" and is not mentioned in BOQ | 75MM DIA NOT REQUIRED
3 | BSR-16.17.56 | Providing & Fixing of C.I. Terminal Guard |  | Rate of 75mm dia Terminal Guard is not mentioned in BOQ | 75MM DIA NOT REQUIRED
4 | BSR-16.17.57 | Providing & Fixing of C.I. Collor |  | Rate of 75mm dia Collor is not mentioned in BOQ | 75MM DIA NOT REQUIRED
5 | BSR-16.17.58 | Providing of Lead Caulked Joints |  | Rate of 75mm dia Lead Caulked Joints is not mentioned in BOQ | 75MM DIA NOT REQUIRED
6 | BSR-16.17.58 | Painting of C.I. Pipe |  | Rate of 75mm dia Pipe Painting is not mentioned in BOQ | 75MM DIA NOT REQUIRED